# Hi Delta FlexGas® - Type WH

## Dual Fuel Water Heaters
Models 302CD-902CD

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

- 100% Factory Fire Tested

- Thermal Efficiency: Up to 85%

- Versa IC® Controller with LCD Display

- Maximum Setpoint: 150°F

- Maximum Outlet Temperature: 200°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal Shock Proof Heat Exchanger

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Cupro-Nickel Heat Exchanger Warranty

- Limited Five-Year Copper Heat Exchanger Warranty

- Full Safety Diagnostics with Fault History

Patent Nos. 6,904,873 & 7,044,124; other patents pending

PolyTuf Powder Coated Cabinet

- No Combustible Floor Shield Required

- Fan-Assisted

Proudly Assembled in the USA

Patented Burner Security Blanket

- Ultra-Low NOx – SCAQMD 1146.2 Certified

- Cascade up to 4 Heaters – No External Sequencer Required

#### Heat Exchanger

Headers

Brass – Standard

A-2 Glass-Lined Cast Iron

ASME Inspected and HLW Stamped
160 PSIG Working Pressure

National Board Approved

Fin Tubing

Copper (Std.) 85%

- Cupro-Nickel 83.1%

ASME Steel Tube Sheet

Silicone High-Temp. O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

Temperature and Pressure Gauge

Water Connections

Left – Standard

A-6 Right Hand

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

Versa IC® Integrated Control

100% Shut-Off/Lockout

Hot Surface Ignition

Ignition Module

- 3-Try – Standard

- C-6 Single-Try

Remote Flame Sensor

Fixed High Limit, Manual Reset 240°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Programmable Pump Time Delays

Heater

Recirculation

Enable/Disable

#### Controls – cont.

LCD Display; Status, Fault and Diagnostics

Cold Water Protection Function

- Optional CWR Variable-Speed Pump

- (See Cat. 5000.73)

Modbus RTU BMS Port (Up to 115K Baud,

- B-85 – BMS Gateway – BACnet MS/TP, BACnet IP, N2 Metasys or Modbus TCP

- B-86 – BMS Gateway – LonWorks

#### Gas Train

Manual Gas Shut-Off Valve(s)

Gas Pressure Regulator

Safety Shut-off Valve

Firing Control Valve

Firing Mode: 2-Stage (WH3)

Natural/Propane Gas

Gas Connection

Left - Standard

Z-1 Right

Design Certified - ANSI Z21.10.3/CSA 4.3

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

Powder Coat Finish

CSA Low Lead Certified (≤ .25% Lead)

#### Venting

Vent Category I/III Cupro-Nickel

Vent Category II/IV Copper

Vent Location

Top – Standard

D-14 Rear

Vent Termination Cap

D-11 Outdoor

D-15 Indoor, Horizontal

Indoor, Vertical (by others)

Combustion Air

D-17 In-Line Filter Kit (TruSeal only)

D-16 Air Intake Elbow

#### Venting – cont.

Extractor – Optional

By others

Not required

#### Burner

Ultra-Low NOx: Less Than 20 PPM

#### Options

C-6	Ignition Module, Manual Rest

D-21	TruSeal Direct Vent

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit Control, Auto Reset

P-  	Pump Bronze

HP, 120V, 1, 60Hz

Water Hardness       GPG
 Mounted	 Loose

Front		 Rear

P-  	Cold Water Run (See 1000.19)

S-1	Low Gas Pressure Switch, Manual

S-2	High Gas Pressure Switch, Manual

X-1	SureRack® Kit

X-2	SureRack Add-on

For Metric information, see Catalog

Additional Options or Accessories

For Metric information, see Catalog

#### Multi-Boiler Temperature Controllers

TempTracker Mod+ Hybrid

B-36, 2-4 Heaters

B-37, 5-10 Heaters

B-38, 11-16 Heaters

B-39 EMS 4-20mA Remote Setpoint Interface Module

B-62 BACnet MS/TP Interface

#### Hi Delta Flex Gas – Type WH
Models 302CD-902CD	Model

3-3/4

NOTE:  Pump location varies based on model and application.

|  | SPECIFICATIONS |  |  |  |  |  |  |  | Approx. Shipping Wt. (lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | MBTUH |  |  | A Width | G NPT | K | W | Amp. Draw* |  |
|  | Input | Output 85% | Output 83.1% |  |  |  |  |  |  |
| 302CD | 300 | 255 | 249 | 36 | 3/4 | 6 | 14-3/4 | 6 | 380 |
| 402CD | 399 | 339 | 332 | 43 | 3/4 | 6 | 18-1/2 | 6 | 445 |
| 502CD | 500 | 425 | 416 | 50 | 1-1/4 | 6 | 22 | 6 | 545 |
| 652CD | 650 | 553 | 540 | 60-1/2 | 1-1/4 | 8 | 27-1/4 | 6 | 590 |
| 752CD | 750 | 638 | 623 | 67-1/2 | 1-1/4 | 8 | 30-3/4 | 6 | 675 |
| 902CD | 900 | 765 | 748 | 78 | 1-1/4 | 8 | 36 | 7 | 740 |

* Without pump

NOTES:	1.	Dimensions are in inches.

2.	Rates shown are for natural or propane gas, and elevations up to 4,500 feet. For installation above 4,500 feet, please contact manufacturer.

3.	Required natural gas pressure is 7 – 10.5” WC. Required propane gas pressure is 11 - 13” WC.

#### Hi Delta Flex Gas – Type WH
Models 302CD-902CD	Model

SHL includes 50 ft of tubing each way (100 total)

** Must use optional cupro-nickel tubes. For hardness exceeding 25 GPG, must use water softener

Basis for minimum flow is 40 GPM or 30°F ∆T, 90 GPM for maximum flow

| Model | 83.1% System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) |
| 302CD | 13 | 40 | 2.0 | 2 | 5.1 | 10 | 50 | 3.0 | 2 | 7.7 | 6 | 90 | 9.8 | 2 | 23.7 |
| 402CD | 17 | 40 | 2.0 | 2 | 5.1 | 13 | 52 | 3.4 | 2 | 8.4 | 7 | 90 | 10.0 | 2 | 23.8 |
| 502CD | 21 | 40 | 2.1 | 2 | 5.2 | 16 | 52 | 3.5 | 2 | 8.6 | 9 | 90 | 10.4 | 2 | 24.2 |
| 652CD | 27 | 40 | 2.2 | 2 | 5.3 | 21 | 52 | 3.7 | 2 | 8.7 | 12 | 90 | 10.8 | 2 | 24.7 |
| 752CD | 28 | 45 | 3.0 | 2 | 6.8 | 23 | 55 | 4.4 | 2 | 9.9 | 14 | 90 | 11.3 | 2 | 25.1 |
| 902CD | 28 | 54 | 4.3 | 2 | 9.7 | 21 | 73 | 7.8 | 2 | 17.2 | 17 | 90 | 11.7 | 2 | 25.5 |

SHL includes 50 ft of tubing each way (100 total)

** Must use optional cupro-nickel tubes. For hardness exceeding 25 GPG, must use water softener

Basis for minimum flow is 40 GPM or 30°F ∆T, 90 GPM for maximum flow

| Model | 85% System Flow and Head Loss |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 3-4 Grains Per Gallon |  |  |  |  | 5-15 Grains Per Gallon |  |  |  |  | 16-25** Grains Per Gallon |  |  |  |  |
|  | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) | ΔT (°F) | GPM | ΔP (FT WC) | MTS (IN) | SHL (FT WC) |
| 302CD | 13 | 40 | 2.0 | 2 | 5.1 | 10 | 50 | 3.0 | 2 | 7.7 | 6 | 90 | 9.8 | 2 | 23.7 |
| 402CD | 17 | 40 | 2.0 | 2 | 5.1 | 13 | 52 | 3.4 | 2 | 8.4 | 8 | 90 | 10.0 | 2 | 23.8 |
| 502CD | 21 | 40 | 2.1 | 2 | 5.2 | 17 | 52 | 3.5 | 2 | 8.6 | 10 | 90 | 10.4 | 2 | 24.2 |
| 652CD | 28 | 40 | 2.2 | 2 | 5.3 | 21 | 52 | 3.7 | 2 | 8.7 | 12 | 90 | 10.8 | 2 | 24.7 |
| 752Cd | 29 | 45 | 3.0 | 2 | 6.8 | 23 | 55 | 4.4 | 2 | 9.9 | 14 | 90 | 11.3 | 2 | 25.1 |
| 902CD | 29 | 54 | 4.3 | 2 | 9.7 | 21 | 73 | 7.8 | 2 | 17.2 | 17 | 90 | 11.7 | 2 | 25.5 |

| Model | 83.1 % Recovery Rates |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 302CD | 1511 | 1007 | 755 | 604 | 504 | 432 | 378 | 336 | 302 |
| 402CD | 2010 | 1340 | 1005 | 804 | 670 | 574 | 502 | 447 | 402 |
| 502CD | 2518 | 1679 | 1259 | 1007 | 839 | 709 | 630 | 560 | 504 |
| 652CD | 3274 | 2182 | 1637 | 1309 | 1091 | 935 | 818 | 727 | 655 |
| 752CD | 3777 | 2518 | 1889 | 1511 | 1259 | 1079 | 944 | 839 | 755 |
| 902CD | 4533 | 3022 | 2266 | 1813 | 1511 | 1295 | 1133 | 1007 | 907 |

| Model | 85 % Recovery Rates |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 100° |
| 302CD | 1545 | 1030 | 773 | 618 | 515 | 442 | 386 | 343 | 309 |
| 402CD | 2055 | 1370 | 1028 | 822 | 685 | 587 | 514 | 457 | 411 |
| 502CD | 2576 | 1717 | 1288 | 1030 | 859 | 736 | 644 | 572 | 515 |
| 652CD | 3348 | 2232 | 1674 | 1339 | 1116 | 957 | 837 | 744 | 670 |
| 752CD | 3864 | 2576 | 1932 | 1545 | 1288 | 1104 | 966 | 859 | 773 |
| 902CD | 4636 | 3091 | 2318 | 1855 | 1545 | 1325 | 1159 | 1030 | 927 |

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com