Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:  	     		Indoor/Outdoor:        	 	MBTUH Input:

TruSeal® Direct Vent

Sealed Combustion Chamber

100% Factory Fire Tested

Efficiency: 84%

Maximum Outlet Temperature: 230°F

Minimum Non-condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Limited Twenty-year Thermal Shock Warranty

Limited Five-year Closed-System Heat Exchanger Warranty

Fault Indicator LED

PolyTuf Powder Coated Cabinet

No Combustible Floor Shield Required

Fan-assisted

#### Heat Exchanger

Headers

Cast Iron, Glass-lined – Standard

Bronze – Option A-1

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Finned Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone High Temp O-Rings

Pressure Relief Valve - ASME

45 PSIG - Standard

PSIG - Optional

Temperature and Pressure Gauge (shipped loose)

Left-hand Water Connections

#### Controls

120V, 60Hz, 1 Power Supply

120/24V 60Hz Transformer

100% Pilot Shutoff/Lockout

Hot Surface Ignition

Remote Flame Sensor

Fixed High Limit Control, Auto Reset

Fixed High Limit Control, Manual Reset

On/Off Power Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Pump Relay

#### Gas Train

Manual Gas Shut-off Valve(s)

Gas Pressure Regulator

Safety Shut-off Valve

Firing Control Valve

Firing Mode

Two-stage (H3) - Standard

On/Off (H4) - Optional

Fuel

Natural Gas

Propane Gas

Design Certified
ANSI Z21.13/CSA 4.9

#### Burner

Ultra-low NOx (<30 ppm)

#### Construction

Indoor/Outdoor Construction

Front Controls Enclosed

PolyTuf Powder Coat Finish

TruSeal® Direct Vent

Filter Kit

#### Venting

Vent Termination Cap

Outdoor – Option D-11

Indoor, Horizontal – Option D-15

Indoor, Vertical (by others)

Combustion Air

Air Intake Elbow – Option D-16

In-line Filter Kit – Option D-17

Extractor – Optional

By others

Not required

#### Temperature Controls

B-3	1-Stage Controller, 100-200°F

B-4	2-Stage Outdoor Reset Control

B-6	2-Stage Controller, 130-230°F

B-  	Remote Controller

By others:

#### Options

F-1	Flow Switch (shipped loose)

F-10	Low Water Cut-off, Remote Probe

I-1	Adjustable High Limit Control, Auto Reset

I-2	Adjustable High Limit Control, Manual Reset

P-  	Pump:      HP, 120V, 160 Hz
 Bronze	 Mounted

Cast Iron	 Loose

X-1	SureRack™ Kit

Two-high

Three-high

#### Hi Delta 122-322

#### Type H - Hydronic Heating 	Model

|  |  |  |  |  |  |  |  |  |  | APPROX. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | MBTUH | AFUE | FIRING | A | B | H | K | T | SHIP WT. |
| MODEL | INPUT | OUTPUT | (%) | STAGES |  |  | NPT |  |  | (LBS.) |
| H 122 | 120 | 101 | 84 | 2* | 24-7/8 | 10-3/4 | 1-1/4 | 4 | 5 | 225 |
| H 162 | 160 | 134 | 84 | 2* | 28-1/2 | 12-9/16 | 1-1/4 | 5 | 5 | 240 |
| H 202 | 199 | 167 | 84 | 2* | 32-1/8 | 14-3/8 | 1-1/4 | 5 | 5 | 255 |
| H 242 | 240 | 202 | 84 | 2* | 35-1/2 | 16-3/16 | 1-1/2 | 5 | 5 | 270 |
| H 322 | 320 | 269 | N/A | 2* | 42-5/8 | 19-13/16 | 1-1/2 | 6 | 5 | 300 |

Dimensions are in inches.	* 1 stage optional

RATES OF FLOW AND PRESSURE DROPS

|  | 10ºF (T | 20ºF (T | 30ºF (T | MIN. FLOW | MAX. FLOW |
| --- | --- | --- | --- | --- | --- |
| MODEL | GPM | (P (ft) | GPM | (P (ft) | GPM | (P (ft) | GPM | (P (ft) | (T | GPM | (P (ft) | (T |
| H 122 | 20 | 2.5 | 10 | <1.0 | N/A | N/A | 10 | <1.0 | 20 | 30 | 5.3 | 7 |
| H 162 | 27 | 4.5 | 13 | 1.1 | N/A | N/A | 10 | <1.0 | 27 | 30 | 5.4 | 9 |
| H 202 | 34 | 7.2 | 17 | 1.85 | 11 | <1.0 | 10 | <1.0 | 34 | 30 | 5.5 | 11 |
| H 242 | 40 | 10.0 | 20 | 2.65 | 14 | 1.3 | 10 | <1.0 | 40 | 44 | 11.8 | 9 |
| H 322 | N/A | N/A | 27 | 4.7 | 18 | 2.2 | 14 | 1.35 | 40 | 44 | 12.2 | 12 |

Basis is 10 GPM or 40°F (T for minimum flow, 44 GPM for maximum flow (except for 1.25” header).

NOTES:	1.	Rates shown are for natural or propane gas, and elevations up to 5,000 feet. For installations above 5,000 feet, please contact manufacturer.

2.	Recommended natural gas pressure is 7 – 10.5” WC. Recommended propane gas pressure is 11 - 13” WC.

# Text boxes

# Hi Delta( - Type H

## Space Heating/Hot Water Boiler Models 122-322

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com