Job:

# ADB™ - Type H

## Hydronic Heating Boiler
Model 500

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

100% Factory Fire Tested

Efficiency: 84%

Maximum Outlet Temperature: 230°F

Minimum Non-condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Footprint: Less than 5 ft2

CSD-1 Gas Train

Limited Twenty-Year Thermal Shock Warranty

Limited Ten-Year Heat Exchanger Warranty

Ten-Year Unconditional Burner Head Warranty

Operation Status Center and Full Diagnostic Panel

#### Heat Exchanger

- Bronze Headers

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Finned Copper Tubes

- ASME Steel Tube Retainer

- Silicone High Temp O-Rings

- Pressure Relief Valve - ASME

60 PSIG – Standard

PSIG – Optional

- Temperature and Pressure Gauge, Shipped Loose

#### Control

- 120V, 60Hz, Power Supply

- 120/24V  60Hz, Transformer

- 100% Pilot Shutoff/Lockout

- Pilot: Electronic Intermittent Ignition (I.I.D.)

- High Limit Control, Manual Reset

- Operating Limit Control, Auto Reset

- On/Off Switch

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Time Delay Pump Off Control

- Central Point Wiring Diagnostics Panel

#### Burner

- Aerodynamically Stabilized Non-clog Burner

- Ultra-low NOx: Less than 30 PPM

#### Gas Train (CSD-1)

- Fuel

Natural Gas

Propane

- Manual Gas Shut-off Valves

- Gas Pressure Regulator

- Safety Shut-off Valve

- Firing Control Valve

- Manual Low Gas Pressure Switch

- On/Off Firing Mode (H4)

- Design Certified ANSI Z21.13/
CSA 4.9

#### Construction

- Indoor/Outdoor Construction

- Enclosed Front Controls

- PolyTuf Powder Coat Finish

- Connections (Water, Electrical, Gas)

Rear – Standard

Right Hand – Option A-8

#### Venting

- Vent Location

Rear – Standard

Right Side – Option Z-2

- Vent Termination Cap

Outdoor - Option D-11

Indoor, Horizontal – Option D-15

Indoor, Vertical (by others)

#### Temperature Controls

B-20	Single-Stage Controller, 
100-200°F

B-6	2-Stage Controller, 
100-200°F

B-21	4-Stage TempTracker 
Digital Controller

B-23	4-Stage TempTracker Digital Controller, Outdoor Reset

Y-241	Electronic Sequencer, 
1-4 Stages

Y-281	Electronic Sequencer, 
5-8 Stages

#### Additional Safety Controls (Optional)

F-10	Low Water Cut-off, 
Remote Probe

S-2	Manual High Gas Pressure Switch

#### Regulatory Agency Requirements

C-5	Ignition Lockout Module

#### Other Equipment

Condensing Heat Exchanger

Pump

ADB - Type H

Model 500

Clearance Requirements

Front	24” (for service)

Rear	1”

Right	12” (water side)

Left	1”

Top	0

Floor	0” *

Vent	1”

*DO NOT install on carpeting

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | #### Ship | #### Foot- |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| #### MODEL | #### MBTUH |  | #### B | #### D | #### E | #### F | #### G | #### H | #### K | #### M | #### N | #### P | #### R | #### T | #### Weight | #### print | #### Amps* |
|  | #### Input | #### Output | #### Height |  |  |  | #### NPT | #### NPT |  |  |  |  |  |  | #### Lbs. | #### Ft.2 |  |
| #### H 500 | #### 500 | #### 420 | #### 49 | #### 46 | #### 30 | #### 22-1/2 | #### 1 | #### 2 | #### 6 | #### 13-3/4 | #### 8-5/8 | #### 40 | #### 22-1/4 | #### 6 | #### 545 | #### 4-3/4 | #### 8 |

Dimensions are in inches.	*	Current draw NOT including pump.

Ratings shown for elevations up to 5,000 feet for natural or propane gas.			(Supply breaker must have a delayed trip)

#### For installation at elevations over 5,000 feet, please consult factory.

#### NOTE:  For direct vent applications, please contact factory about relocating the pump.

BOILER RATES OF FLOW AND PRESSURE DROPS

|  | 20°F T |  | MAX. FLOW |  |  | MIN. FLOW |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ###### MODEL | ###### GPM | P (ft) | ###### GPM | P (ft) | ###### T | ###### GPM | P (ft) | ###### T |
| H 500 | 42 | 2.6 | 84 | 8.8 | 10°F | 30 | 1.6 | 28°F |

Recommended natural gas pressure is 7-10.5” w.c.

#### Recommended propane gas pressure is 11-13” w.c.