### DIVISION 23 52 33.13

### FINNED WATER-TUBE WATER HEATERS

- GENERAL

SUMMARY

Section includes gas-fired, copper finned-tube water heaters for use with a storage tank.

Related Sections

Specifier Note:  Use as needed

Building Services Piping – Division 23 21 00

Breeching, Chimneys, and Stacks (Venting) – Division 23 51 00

HVAC Instrumentation and Controls – Division 23 09 00

Electrical – Division 23 09 33

REFERENCES

ANSI Z21.10.3/CSA 4.3

ASME, Section IV

2006 UMC, Section 1107.6

National Fuel Gas Code

NEC

SUBMITTALS

Product data sheet (including dimensions, rated capacities, shipping weights, accessories)

Wiring diagram

Warranty information

Installation and operating instructions

QUALITY ASSURANCE

Regulatory Requirements

ANSI Z21.10.3/CSA 4.3

Local and national air quality regulations for low NOx (0-55 PPM NOx emissions) water heaters

Certifications

CSA

ASME HLW Stamp and National Board Listed

heat exchanger WARRANTY

Limited five-year warranty from date of installation

Limited twenty-year thermal shock warranty from date of installation

Limited ten-year warranty for cupro-nickel heat exchangers only

- PRODUCTS

MANUFACTURER

Raypak, Inc.

Contact: 2151 Eastman Ave., Oxnard, CA 93030; Telephone: (805) 278-5300; 
Fax: (800) 872-9725; Web site: www.raypak.com

Product: Raytherm® Low NOx copper finned-tube water heater(s) (Models 181-401)

WATER HEATERS

General

The water heater(s) shall be fired with               gas at a rated input of               BTU/hr.

The water heater(s) shall be CSA tested and certified with a minimum thermal efficiency of 82 percent at full fire.

The water heater(s) shall be ASME inspected and HLW-stamped and National Board registered for 160 PSIG working pressure, complete with a Manufacturer's Data Report.

The water heater(s) shall have a floor loading of 70 lbs. /square foot or less.

Heat Exchanger

The heat exchanger shall be of a single-bank, horizontal-grid design with integral copper fin tubes, each end of which is rolled into an ASME boiler-quality steel tube sheet.

The heat exchanger shall be sealed to 160 PSIG rated bronze headers with high temperature silicone "O" rings.

The low water volume heat exchanger shall be explosion-proof on the water side and shall carry a twenty-year warranty against thermal shock.

The headers shall be secured to the tube sheet by stud bolts with flange nuts to permit inspection and maintenance without removal of external piping connections.

The heat exchanger shall incorporate “V” baffles, between the tubes, to ensure complete contact of the external tube surfaces with the products of combustion.

The water heater(s) shall be capable of operating at inlet water temperatures as low as 105°F without condensation.

The water heater(s) shall be designed to accommodate field changes of either left or right hand plumbing and electrical while leaving the tube bundle in place.

The heat exchanger shall be AB-1953 compliant in construction and verification by a third party certification agency.

Burners

The stainless steel alloy burners shall have lanced ports and slots, utilize multiport radial gas orifices, and be capable of quiet ignition and extinction without flashback at the orifice.

Pilot Control System

The water heater(s) shall be equipped with a 100 percent safety shutdown system and an electronic intermittent ignition system with electronic flame supervision having a nominal 0.8 second flame response time.

The ignition shall be Spark Ignition type with full flame rectification to ensure consistent operation.

The igniter will be located away from the water inlet to protect the device from condensation during startup.

The ignition control module shall include two LEDs that indicate flame presence and/or system status.

Gas Train

The water heater(s) shall have dual-seated main gas valve(s).

Gas control trains shall have a redundant safety shut-off feature, main gas regulator, shut-off cock and plugged pressure tapping to meet the requirements of ANSI Z21.10.3/CSA 4.3.

Water Heater Control

The following safety controls shall be provided:

High limit control

Flow switch, mounted and wired

____PSIG ASME pressure relief valve, piped by the installer to an approved drain

Temperature and pressure gauge

The water heater(s) shall be equipped with an energy-saving pump control relay (Economaster), mounted and wired, which automatically shuts off the water heater pump at a set period after water heater shut-down (adjustable from three to ten minutes) to avoid standby losses associated with constant pump operation.

Firing Mode

The water heater(s) shall be equipped to (a) or (b):

Provide on/off control of the gas input to the water heater.

Provide staged control of the gas input to the water heater.

Water Heater Diagnostics

Provide ignition module indicating the following heartbeats (flashes) by LED signal:

“M” Ignition Model (Continuous Retry)

2 flashes per second (“heartbeat”) – Normal operation

2 flashes – Five-minute retry delay

3 flashes – Recycle; flame failed during run

4 flashes – Flame sensed out of sequence

7 flashes – Flame sense leakage to ground

8 flashes – Low 24VAC (secondary voltage)

6+2 flashes – Five-minute retry delay (on every third retry on the same “Call For Heat”)

6+3 flashes – On every sixth flame failure during run on the same “Call For Heat”

6+4 flashes – Flame sensed out of sequence for more than 10 seconds

ON steady – Soft lockout due to error detected during self-check sequences

“H” Ignition Model (Lockout)

2 flashes per second (“heartbeat”) – Normal operation

        - 2 flashes – Five-minute retry delay

        - 3 flashes – Recycle; flame failed during run

        - 4 flashes – Flame sensed out of sequence

        - 7 flashes – Flame sense leakage to ground

        - 8 flashes – Low 24VAC (secondary voltage)

        - 6+2 flashes – Failed trial for ignition resulting in lockout

        - 6+3 flashes – More than five flame failures during run on the same “Call For Heat” resulting in lockout

        - 6+4 flashes – Flame sensed out of sequence for more than 10 seconds

        - ON steady – Soft lockout due to error detected during self check sequences

Combustion Chamber: The high-temperature, multi-piece, interlocking castable combustion chamber liner shall reduce standby radiation losses, reducing jacket losses and increasing unit efficiency.

Venting

When routed vertically, the water heater’s flue material and size shall be in accordance with the National Fuel Gas Code, ANSI Z223.1/NFPA54 latest edition (Category I).

Cabinet

The corrosion-resistant galvanized steel jackets shall be finished with a baked-on epoxy powder coat which is suitable for outdoor installation, applied prior to assembly for complete coverage, and shall incorporate louvers in the outer panels to divert air past heated surfaces.

The water heater(s), if located on a combustible floor, shall require an optional separate combustible floor base.

Specifier Note:	The remaining items in this section are options. Delete those that are not being specified. IMPORTANT: The Cold Water Start and Cold Water Run Systems cannot be used on the same water heater.

Operating Controls

The water heater(s) shall feature an optional temperature controller.

Water Heater Pump - Refer to Equipment Schedule

Cold Water Start System

The water heater(s) shall be configured with a cold water start automatic proportional bypass system that ensures the water heater will experience inlet temperatures in excess of 105ºF within 7 minutes to avoid damaging condensation. The unit will automatically shut down if the inlet temperature is not achieved within the 7-minute time frame.

The cold water start system shall be configured with a modulating three-way valve that is controlled by a system-matched PID controller. The PID controller temperature sensor shall be located in the inlet header of the water heater.

The control shall have a temperature setting dial located on the face of the board. The temperature range of the dial shall be 105ºF to 120ºF. The PID Logic shall be capable of limiting system overshoot to a maximum of 10ºF on initial start-up or call-for-heat.

The cold water start system shall be completely wired and mounted at the factory.

The control shall have the following diagnostic LED’s:

Call for heat

Start-up mode

Inlet temperature error

Sensor out of range

The controller shall have alarm contacts.

Cold Water Run System

The water heater(s) shall be configured with a cold water run automatic proportional bypass system that ensures the water heater will experience inlet temperatures in excess of 105ºF within 7 minutes to avoid damaging condensation. The unit will automatically shut down if the inlet temperature is not achieved within the 7-minute time frame.

The cold water run system shall be configured with a variable speed pump that is controlled by a system-matched PID control that injects the correct amount of cold water directly into the water heater loop to maintain a minimum inlet temperature. The PID controller temperature sensor shall be located in the inlet header of the water heater.

The control shall have a temperature setting dial located on the face of the board. The temperature range of the dial shall be 105ºF to 120ºF. The PID Logic shall be capable of limiting system overshoot to a maximum of 10ºF on initial start-up or call-for-heat.

The cold water run system shall be completely wired and mounted at the factory.

The control shall have the following diagnostic LED’s:

Call for heat

Start-up mode

Inlet temperature error

Sensor out of range

The controller shall have alarm contacts.

SOURCE QUALITY CONTROL

The water heater(s) shall be completely assembled, wired, and fire-tested prior to shipment from the factory.

The water heater(s) shall be furnished with the sales order, ASME Manufacturer’s Data Report, inspection sheet, wiring diagram, rating plate and Installation and Operating Manual.

- EXECUTION

INSTALLATION

Must comply with:

Local, state, provincial, and national codes, laws, regulations and ordinances

National Fuel Gas Code, NFPA 54/ANSI Z223.1 – latest edition

National Electrical Code, ANSI/NFPA 70 – latest edition

Canada only: CAN/CSA B149 Installation Code and CSA C22.1 CEC Part I

Manufacturer’s installation instructions, including required service clearances and venting guidelines

Manufacturer’s representative to verify proper and complete installation.

START-UP

Shall be performed by Raypak factory-trained personnel.

Test during operation and adjust if necessary:

Safeties (2.2 - F)

Operating Controls (2.3)

Static and full load gas supply pressure

Gas manifold and blower air pressure

Submit copy of start-up report to Architect and Engineer.

training

Provide factory-authorized service representative to train maintenance personnel on procedures and schedules related to start-up, shut-down, troubleshooting, servicing, and preventive maintenance.

Schedule training at least seven days in advance.

END OF SECTION

# Text boxes

Catalog No.:	3500.92D

Effective:	04-15-10

Replaces:	06-1-08

RAYTHERM( LOW NOX, TYPE WH
SUGGESTED SPECIFICATIONS