# XTherm® - Type H

## Heating Boilers

## Models 1005A-2005A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 96% Thermal Efficiency at Full Rate

- 100% Factory Fire Tested

- VERSA IC® Modulating Controller with 7” color touchscreen display

- Raymote™ remote connectivity provided standard

- Full Electronic Modulation, Constant Ratio 7:1 Turndown

- Full Safety Diagnostics with History

- Status Display Lights

- Cascade up to 4 Heaters – No External Sequencer Required

- Modbus RTU BMS Port

- Maximum Outlet Water Temperature: 235°F

- Minimum Inlet Water Temperature: 50°F

- Limited Twenty-Five-Year Thermal Shock Warranty

Proudly Assembled in the USA

Limited Ten-Year Primary Heat Exchanger Warranty

- Limited Ten-Year Secondary Heat Exchanger Warranty

#### Heat Exchanger

Headers

Cast Iron – Standard

Bronze – Option A-1

ASME H Stamped; 160 PSIG MAWP

National Board Listed

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Powder-Coated Tube Sheet

Silicone High Temp O-Rings

ASME Pressure Relief Valve

60 PSIG – Standard

PSIG – Optional

Manual Air Bleed

T&P Gauge

Secondary Stainless Steel Condensing Heat Exchanger – U stamped

Stainless Steel Evaporator Plate

Boiler Pump: 120V, 1, 60Hz;

Cast Iron – Standard

Bronze – Option

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

VERSA IC®

7” color HD touchscreen display

Raymote™ Wi-Fi remote connectivity

Ignition Module

3-Try – Standard

C-6 Single-Try – Optional

Remote Flame Sensor

Fixed High Limit, Manual Reset, 240°F

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Freeze Protection

* Requires 200ºF Manual Reset High Limit & 180ºF Max Setpoint

Alarm Dry Contact

Pump Outputs – Pilot Duty

DHW Indirect

System

Programmable Pump Time Delays

Modulating Temperature Control; 7:1 turndown

Water Temperature Sensors (7)

Cold Water Protection – Built In

Blocked Condensate Switch

Modbus RTU BMS Port (Up to 115K Baud Rate, see Cat. No. 5000.73)

- B-85   BMS Gateway, Modbus RTU to Modbus TCP, N2 Metasys, BACnet IP, or BACnet MS/TP

- B-86   BMS Gateway, Modbus RTU to LonWorks

#### Burner

Hot Surface Ignition (HSI)

Radially Fired Knitted Burner

#### Gas Train

Fuel

Natural Gas

Propane (Grade HD-5)

Dual-Seat Combination Valve

Manual Shut Off Firing Valve

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

Rear Connections (Water, Gas, Vent, Electrical, Comb. Air, Cond. Drain)

Combustion Air Filter

Design Certified ANSI Z21.13/CSA 4.9

Front Connection Low Voltage Wiring

#### Venting

Vent Termination, Cat IV

D-11 Outdoor or Indoor, Vertical

D-15  Indoor, Horizontal

Extractor – Optional, Cat II

By others

Not required

#### Options

D-32*	PVC Vent Adapter

(Includes 162ºF Manual Vent Limit) (Factory installed only)

D-33	Centrotherm™ Polypropylene Vent Adapter (Includes 180ºF

Manual Vent Limit) (shipped loose)

F-10	Low Water Cut-Off, Remote Probe

I-1	High Limit, Auto Reset, Adj., 
100-240°F

I-2	High Limit, Manual Reset, Adj., 100-240°F

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

#### Multi-Boiler Digital Temp Controllers

B-36	TempTracker Mod+ Hybrid, 
2-4 Boilers, OA Reset

B-37	TempTracker Mod+ Hybrid, 
5-10 Boilers, OA Reset

B-38 	TempTracker Mod+ Hybrid, 
11-16 Boilers, OA Reset

B-39* 	EMS 4-20 mA Remote Setpoint Interface Module

B-62* 	BACnet MS/TP Interface Module (*only used with B-36 to B-38)

XTherm – Type H

Models 1005A-2005A	Model

NOTE:  Primary/Secondary plumbing is mandatory for proper operation.

CLEARANCES (in.)

|  | Front | Rear | Right | Left | Top | Floor | Vent |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Certified Minimum | 24 | 12 | 1 | 1 | 0 | 0 | 1 |
| Minimum Service | 24 | 36 | 24 | 1 | 10 | N/A | N/A |

| Model | Amp Draw** |  |
| --- | --- | --- |
|  | Boiler † | Pump † |
| 1005A | 12** | 10 |
| 1505A | 12** | 14 |
| 2005A | 18** | 17 |

† Separate power connections are factory supplied and separate supply breakers must be field supplied.

** Current draw is for boiler only (Supply breaker must have delayed trip).

| Model (H7-) | MBTUH |  | Dimensions (in) |  |  |  |  |  |  |  |  |  |  |  | Ship Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B Height | D | E | F | G* NPT | K Flue Ø | L | M | N C/A Ø | P | R | Y |  |
|  | Input | Output |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1005A | 999 | 959 | 55-1/8 | 45 | 47-1/8 | 36-1/2 | 1-1/4 | 6 | 40-1/16 | 11-1/2 | 6 | 47-1/8 | 8-1/16 | 6-1/16 | 1065 |
| 1505A | 1500 | 1440 | 67-1/8 | 57 | 59-1/16 | 38-1/2 | 1-1/4 | 8 | 52-1/16 | 12-5/8 | 8 | 59-1/8 | 8-3/16 | 6-1/16 | 1234 |
| 2005A | 1999 | 1919 | 81-1/8 | 71 | 71-3/16 | 38-1/2 | 2 | 8 | 64-1/16 | 12-5/8 | 8 | 73-1/8 | 8-3/16 | 6-1/4 | 1461 |

| Note: Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions. | * For Propane Gas, all models are 1” NPT |
| --- | --- |

| System Return Temp (ºF) | Model 1005A |  |  | Model 1505A |  |  | Model 2005A |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Supply Temp1 (ºF) | Minimum Pipe Size2 |  | Supply Temp1 (ºF) | Minimum Pipe Size2 |  | Supply Temp1 (ºF) | Minimum Pipe Size2 |  |
|  |  | <80’ eq | 80-200’ eq |  | <80’ eq | 80-200’ eq |  | <80’ eq | 80-200’ eq |
| 60 | 138 | 2” NPT | 2-1/2” NPT | 147 | 2” NPT | 2-1/2” NPT | 154 | 2” NPT | 2-1/2” NPT |
| 80 | 138 | 2” NPT | 2-1/2” NPT | 147 | 2” NPT | 2-1/2” NPT | 154 | 2-1/2” NPT | 3” NPT |
| 100 | 138 | 2-1/2” NPT | 3” NPT | 147 | 2-1/2” NPT | 3” NPT | 154 | 2-1/2” NPT | 3” NPT |
| 120 | 145 | 2-1/2” NPT | 3” NPT | 158 | 2-1/2” NPT | 3” NPT | 170 | 2-1/2” NPT | 3” NPT |
| 140 | 165 | 2-1/2” NPT | 3” NPT | 178 | 2-1/2” NPT | 3” NPT | 190 | 2-1/2” NPT | 3” NPT |
| 160 | 185 | 2-1/2” NPT | 3” NPT | 198 | 2-1/2” NPT | 3” NPT | 210 | 2-1/2” NPT | 3” NPT |

1 – Approximate high fire heater outlet temperature based on the standard heater pump and recommended connecting pipe size.

2 – Minimum pipe size based on total equivalent feet of supply and return piping between the system loop and heater.