# Y-Series Electronic Boiler Control

# Sample Specification

Section I: General Requirements

1.	Provide a Raypak Y-Series Electronic Boiler Control System capable of controlling            (   ) Raypak Model      		copper finned tube boiler(s).The electronic boiler control system shall consist of a boiler control module, a water temperature sensor and an outdoor air temperature sensor. An internal power transformer shall be integral to the boiler control module.

2.	The system water temperature and outdoor air sensors shall be redundant element thermistors capable of maintaining ±1°F sense accuracy when installed with a maximum of 300 feet of shielded cable as recommended by the manufacturer.

3.	The boiler control shall be listed by UL as an Energy Management System.

4.	The boiler control shall carry a one year limited warranty against failure caused by defective workmanship or material.

5.	The boiler(s) and control system shall be manufactured by the same company and shall carry single source responsibility.

Section II: Equipment Enclosure

1.	The boiler control module shall be boiler or remote mountable in a NEMA 3R rated rain proof gasketless enclosure. The lockable control enclosure shall be constructed of 18 gauge steel and shall be vandal and tamper resistant. The access door of the enclosure, once unlocked, shall be easily removable without the use of tools.

2.	The outdoor air temperature sensor shall be mounted in a protective steel housing.

3.	All exterior enclosure surfaces shall be protected with a baked-on UV inhibited Polytuff powder coat finish.

Section III: Control Functions

1.	The boiler control system shall be microprocessor based and shall control the firing sequencing of the boiler(s) to meet the system demand within the selectable limits of the Control Band, the Setpoint, the outdoor temperature, and the Reset Ratio.

2.	The boiler control's operational algorithm shall have an advanced Proportional plus Integral plus Derivative (PID) logic structure. The control algorithm shall automatically optimize boiler response based on a history file of the last 48 firings.

3.	The microprocessor shall be self-checking and shall incorporate a System Test Switch for manual testing.

4.	Boiler lead/lag selection will be performed automatically using a First-on First-off protocol or manually by dip switches.

5.	The boiler control shall have a primary pump control output. An energy saving Pump Off Delay function shall be an integral part of the primary pump control.

6.	The system shall incorporate an outdoor cutoff function that shuts down the boiler(s) and the primary system pump when the outdoor air temperature exceeds a user adjustable setpoint.

7.	The boiler control shall have a manual override function that allows independent operation of the boiler(s) or specific stages for maintenance or in case of catastrophic boiler control failure.

8.	[Optional Alternate Setpoint Configuration - Setback] The boiler control shall have an independent alternate setpoint potentiometer that is activated by an alternate setpoint timer. The alternate setpoint timer shall be a 7 day electromechanical clock with activation times at one hour intervals. The setpoint timer will allow up to 168 setback periods per week. A manual alternate setpoint override switch will allow operation at either the setpoint or alternate set point.

Section IV: Adjustable Parameters

1.	The boiler control shall have front mounted, knob operated adjustments for the following parameters:

- Reset Ratio shall be adjustable from 0.12:1 to 8:1;

- Control Band shall be adjustable from 1° to 10°F;

- Primary Pump Off Delay shall be adjustable from 0 to 10 minutes;

- Outdoor Cutoff Temperature shall be adjustable from 32° to 200°F;

- Outdoor Cutoff Deadband shall be adjustable from 1° to 10°F;

- Boiler On Delay shall be adjustable from 0 to 5 minutes;

- Stage On Delay shall be adjustable from 0 to 60 seconds;

- Maximum Water Temperature shall be adjustable from 70° to 235°F;

- Setpoint shall be adjustable from 40° to 220°F. Setpoint will have a factory set protective minimum Setpoint of 105°F to prevent steady state condensation in the boiler. The protective minimum set point can be overridden by dip switch to provide complete Setpoint range adjustment.

Section V: Display Functions

1.	The control shall incorporate the following LED operating and diagnostic lights:

- Control On shall indicate that the control is powered and is not in outdoor cutoff mode;

- Pump shall indicate that the primary pump circuit is energized;

- Call For Heat shall indicate that a signal is present at the thermostat inputs;

- Setting Error shall provide indication of an improper board or setting configuration;

- Sensor Error shall indicate an out of range reading from either the outdoor air temperature sensor or the water temperature sensor;

- Eight Stage LED's shall indicate which of up to eight stages is firing.

2.	Optional LCD readout display panel.