Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

# Power Vent

# For Raytherm®
Models 181-401 & 182-400

Versatile

Suitable for use with hydronic heating boilers
and hot water heaters

Permits sidewall venting

Allows use of vent pipe as small as 4" in diameter

Efficient

Maintains thermal efficiency of 82% on all 
appliance sizes

Multi-Position Capability

90° elbow rotates to align fan discharge with 
vent pipe and reduce the number of fittings required

# Features

- Induced draft

- Plenum sized for appliance capacity

- Air flow proving switch, mounted and wired

- Fan motor relay, mounted and wired

- 115/230 Volt, 60 Hertz, 1.95/1.0 Amp, 130 CFM Max., 3200 RPM motor; Factory-wired for 115 Volts

- 90° elbow can be used as a termination cap for horizontal venting

- Heavy-duty galvanized steel cabinet

- Polytuf powder coat finish

- Indoor/Outdoor construction

- Easy installation

- Limited one-year warranty

- Shipped loose for field mounting

#### Power Vent

#### For Raytherm 181-401 & 182-400	Model

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

NOTES:

- All units can exhaust flue gases at:

Horizontal

Up to 40 ft. of equivalent length vent pipe

90° elbow = 10 ft. equivalent length
45° elbow = 5 ft. equivalent length

Vertical

Up to 40 ft. straight vertical venting

For vents above 40 ft., a barometric damper is required.

2.	Vent pipe must meet Category III appliance venting requirements.

3.	Vent pipe sizes are based 300°F nominal flue temperature and sea-level operation. For installation under other conditions, please consult the factory.

| Raytherm Model | Part Number | Dimensions (in.) |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | A | B | C | D |
| 181/182 | 008757 | 18-1/8 | 12-3/8 | 7-7/8 | 4-1/4 |
| 261/260 | 008757 | 18-1/8 | 12-3/8 | 7-7/8 | 4-1/4 |
| 331/330 | 008758 | 17-1/2 | 15-3/4 | 7-5/8 | 6 |
| 401/400 | 008758 | 17-1/2 | 15-3/4 | 7-5/8 | 6 |