# XPAK-FT®

# Condensing Boiler

## Hydronic Heating Boilers

## Residential - Commercial

## Models 88AR, 108AR, 198AR, 278AR & 398A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model:

VERSA IC® Integrated Control Platform

Soft Start, Electronic Modulation, up to 10:1 Turndown

LCD Status Display with Full Diagnostics and Fault Memory

Zero Clearance to Combustibles

3-in-1 Vent adapter (PVC/CPVC - Duravent® Polypro - SS)

Meets 2012 NOx Requirements (< 14 ng/J (< 55 PPM NOx))

Maximum Outlet Water Temperature: 195ºF

Maximum System Temperature: 190ºF

Limited 25-Year Thermal Shock Warranty

Proudly Assembled in the USA

Limited 10-Year Heat Exchanger Warranty

Modbus RTU RS485 Port

#### Heat Exchanger

- All Stainless Steel Construction

- Gasketless Heat Exchanger Design

- ASME H Stamped
80 PSIG Working Pressure

- National Board Approved

- ASME Pressure Relief Valve

30 PSIG – Standard

- Temperature and Pressure Gauge,
Shipped Loose

#### Control

- 120V, 60Hz, 1Ø, Power Supply

- Versa IC Operating Control with LCD display.

- Outdoor reset with Indirect Priority

- 0-10 VDC input for BMS

- Cascade up to 4 boilers

- Spark Ignition (DSI)

- Remote Flame Sensor

- High Limit, Manual Reset, Fixed, 200ºF

- Alarm Dry Contact Connection

- On/Off Power Switch

- Blocked Vent Pressure Switch

- Boiler, DHW & System Pump Contacts

- Water Temperature Sensors (4)10kΩ (2 shipped loose)

- Outdoor Air Sensor (1) 10kΩ (shipped loose)

#### Burner

- Ultra-Low NOx: Less than 14 ng/J

#### Gas Train

- Fuel

Natural Gas

Propane

- Dual-Seat Combination Valve

- Electronic Modulating Firing Mode (H7)

#### Construction

- Indoor Construction

- Front Controls Enclosed

- PolyTuf Powder Coat Finish

- Bottom Connections (Electrical, Gas, Water)

- Top Connections (Combustion Air, Vent)

- Design Certified ANSI Z21.13/
CSA 4.9

- Condensate Trap

#### Venting (PVC/CPVC*-Duravent Polypropylene – Centrotherm Polypropylene – Stainless Steel)

- Vent Termination

D-11 - SS Termination

D-94 - Horizontal twin pipe Poly

D-95 - Horizontal Concentric Poly

D-96 - Vertical Concentric Poly

D-92 - Polypro reducer (88AR & 398A only)

#### Options – Shipped Loose

F-1 	Flow Switch – (Loose)

F-10 	Low Water Cut-Off, Manual Reset (88AR to 278AR)

P-  	Pump:      HP, 120V,1, 60Hz

Cast Iron

Bronze/SS

S-1/S-2  High/Low Gas Pressure Switch, Manual Reset

Z-12	Condensate Neutralizer Kit

#### Additional Options or Accessories

*Configured for PVC Vent Standard. Maximum System Temperature of 170ºF for PVC Vent.

Raypak® XPak-FT® Residential

Residential - Commercial

Condensing Boiler	Model

Models 88AR, 108AR, 198AR, 278AR & 398A

| Model No. | A | B | C | D | E | F | H | J | K | L | M | N | P |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 88AR | 16-7/16 | 35-7/8 | 16-1/2 | 2-1/8 | 2-3/4 | 6-3/8 | 7-7/8 | 9-1/2 | 5-1/2 | 1-1/2 | 4-5/8 | 2-7/8 | 2-3/8 |
| 108AR |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 198AR | 18-5/8 | 36-1/4 | 19-7/16 | 2 | 3-1/8 | 8-1/4 | 10 | 11-3/8 | 7-1/8 | 1-3/4 | 12-3/8 | 3-5/8 | 2-3/8 |
| 278AR |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 398A | 21-7/16 | 38-5/8 | 22-1/8 | 2-3/4 | 4 | 10-1/8 | 12 | 13 | 8-15/16 | 2-5/8 | 15-3/8 | 4 | 2-1/8 |

| Model No. | AFUE Rating |  |  | Minimum Operating Input (MBH) | Water Conn. (NPT) | Gas Conn. (NPT) |  | Vent Size (In.) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input (MBH) |  | % |  |  | Nat. | Pro. | Flue | Intake |
|  | Min | Max |  |  |  |  |  |  |  |
| H7-88AR | 17.0 | 85.0 | 95 | 12.0 | 1” | 1/2” | 1/2” | 2” / 3” ** | 2” / 3” ** |
| H7-108AR | 22.0 | 110.0 | 95 | 13.0 | 1” | 1/2" | 1/2" | 3” | 3” |
| H7-198AR | 39.8 | 199.0 | 95 | 28.4 | 1-1/4” | 3/4" | 3/4" | 3” | 3” |
| H7-278AR | 55.0 | 275.0 | 94.8 | 36.6 | 1-1/4” | 3/4” | 3/4” | 3” | 3” |
| H7-398A | 39.9 | 399.0 | 96* | 39.9 | 1-1/2” | 3/4” | 3/4” | 3” / 4” *** | 3” / 4” *** |

*Model 398A value is Thermal Efficiency.

**Model 88AR vent is 3” standard and can be reduced to 2” with shorter run.

***Model 398A vent is 4” standard and can be reduced to 3” with shorter run.

| Model No. | Maximum Flow |  |  | Minimum Flow |  |  | 30ºF ΔT |  | 40ºF ΔT |  | 50ºF ΔT |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | GPM | ΔP (ft) | ΔT | GPM | ΔP (ft) | ΔT | GPM | ΔP (ft) | GPM | ΔP (ft) | GPM | ΔP (ft) |
| H7-88AR | 8.1 | 5.4 | 20 | 2.7 | 1.4 | 60 | 5.4 | 3.3 | 4.0 | 2.3 | 3.2 | 1.8 |
| H7-108AR | 10.5 | 7.4 | 20 | 3.5 | 2.0 | 60 | 7.0 | 4.5 | 5.2 | 3.2 | 4.2 | 2.4 |
| H7-198AR | 18.9 | 11.6 | 20 | 6.3 | 3.0 | 60 | 12.6 | 6.2 | 9.5 | 4.3 | 7.6 | 3.5 |
| H7-278AR | 26.1 | 20.3 | 20 | 8.7 | 4.0 | 60 | 17.4 | 10.1 | 13.1 | 6.5 | 10.5 | 4.9 |
| H7-398A | 38.3 | 14.1 | 20 | 12.8 | 3.4 | 60 | 25.5 | 7.4 | 19.2 | 5.0 | 15.3 | 4.0 |

| Model No. | Standard Boiler Pump * |  |
| --- | --- | --- |
|  | Pump | HP |
| H7-88AR | Taco 007 | 1/25 |
| H7-108AR | Taco 007 | 1/25 |
| H7-198AR | Taco 0010 | 1/8 |
| H7-278AR | Taco 0012 | 1/8 |
| H7-398A | Taco 0012 | 1/8 |

*Pump selection based on 30ºF ΔT with up to 50 eq. ft. of tubing

Raypak, Inc. 2151 Eastman Avenue, Oxnard, CA  93030 (805) 278-5300 Fax (800) 872-9725   www.raypak.com