Job:

# ADB™ - Type H

## Hydronic Heating Boilers

Models 751-1501

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

100% Factory Fire Tested

- Efficiency: 84%

- Maximum Outlet Temperature: 230°F

- Minimum Non-Condensing Inlet Temperature: 105°F

- Thermal Shock Proof Heat Exchanger

- Footprint: Less Than 5-1/2 ft2

- Limited Twenty-Year Thermal Shock Warranty

- Limited Ten-Year Heat Exchanger Warranty

- Ten-Year Unconditional Burner Head Warranty

- Operation Status Center and Full Diagnostic Panel

#### Heat Exchanger

- Bronze Headers

- ASME Inspected and Stamped
160 PSIG Working Pressure

- National Board Approved

- Copper-finned Tubes

- ASME Steel Tube Retainer

- Silicone High Temp O-Rings

- 60 PSIG ASME Pressure Relief Valve

- Temperature and Pressure Gauge,
Shipped Loose

#### Control

- 120V, 60Hz, Power Supply

- 120/24V 60Hz Transformer

- 100% Pilot Shutoff/Lockout

- Electronic Intermittent Ignition Pilot (IID)

- High Limit Control, Manual Reset

- High Limit Control, Auto Reset

- On/Off Switch

- Flow Switch

- Blocked Vent Pressure Switch

- Combustion Air Proving Switch

- Time Delay Pump Off Control

- Central Point Wiring Diagnostics Panel

#### Burner

- Aerodynamically Stabilized
Non-Clog  Burner

- Ultra-Low NOx: Less than 30 PPM

#### Gas Train

- Fuel

Natural Gas

Propane (Models 751 & 1001)

- Manual Gas Shut-off Valves

- Gas Pressure Regulator

- Safety Shut-off Valve

- Firing Control Valve

- Manual Low Gas Pressure Switch

- On/Off Firing Mode (H4)

- Design Certified ANSI Z21.13/
CSA 4.9

#### Construction

- Indoor/Outdoor Construction

- Front Controls Enclosed

- PolyTuf Powder Coat Finish

- Connections (Water, Electrical, Gas)

Rear – Standard

Right Side – Option A-8

#### Venting

- Vent Location

Rear – Standard

Right Side – Option Z-2

- Vent Termination Cap

Outdoor - Option D-11

Indoor, Horizontal – Option D-15

Indoor, Vertical (by others)

#### Temperature Controls

B-20	Single-Stage Controller, 
100-200°F

B-6	2-Stage Controller, 100-200°F

B-21	4-Stage TempTracker Digital Controller, Loose

B-23	4-Stage TempTracker Digital Controller, Outdoor Reset, Loose

Y-241	Electronic Sequencer, 
1-4 Stages

Y-281	Electronic Sequencer, 
5-8 Stages

#### Additional Safety Controls (Optional)

F-10	Low Water Cut-off, 
Remote Probe

S-2	Manual High Gas Pressure Switch

#### Regulatory Agency Requirements

C-5	Ignition Lockout Module

#### Other Equipment

Condensing Heat Exchanger

Pump

ADB – Type H

Models 751-1501	Model

Raypak, Inc.    2151 Eastman Avenue, Oxnard, CA  93030    (805) 278-5300    Fax (800) 872-9725    www.raypak.com

Certified Clearances

Front	24” (for service)

Rear	12” (water side)

Right	1”

Left	1”

Top	0” (see note 1)

Floor	0” (see note 2)

Vent	1”

Notes:

1.	24” required for service

2.	DO NOT install on carpeting

| Model | MBTUH |  | B | D | E | F | G | H | K |  | M | P | Ship Weight | Foot-print | Amps* |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | Height |  |  |  | NPT | NPT | Flue  |  |  |  | (Lbs.) | (Ft2) |  |  |
| H 751 | 750 | 630 | 64 | 38 | 44-1/2 | 29-3/4 | 1-1/2 | 2 | 8 |  | 17-3/4 | 41 | 680 | 5.4 | 8 |  |
| H 1001 | 999 | 840 | 72 | 46 | 52-1/2 | 37-3/4 | 1-1/2 | 2-1/2 | 10 |  | 21-1/2 | 49 | 720 | 5.4 | 10 |  |
| H 1501 | 1499 | 1260 | 82 | 56 | 62-1/2 | 47-3/4 | 1-1/2 | 2-1/2 | 12 |  | 20-1/4 | 59 | 780 | 5.4 | 12 |  |
| - Dimensions are in inches. - Ratings shown are for elevations up to 5,000 feet. For installations at elevations above 5,000 feet, please consult the factory for additional instructions. - For direct vent applications, please contact the factory about relocating the pump. |  |  |  |  |  |  |  |  |  | * Current draw does NOT include pump. (Supply breaker must have delayed trip.) |  |  |  |  |  |  |

RATES OF FLOW AND PRESSURE DROPS

|  | 20°F T |  | 30°F T |  | 40°F T |  | Maximum Flow |  |  | Minimum Flow |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model | GPM | P (ft.) | GPM | P (ft.) | GPM | P (ft.) | GPM | P (ft.) | T (°F) | GPM | P (ft.) | T (°F) |
| H 751 | 63 | 5.8 | 42 | 2.9 | 32 | 1.8 | 110 | 17.0 | 11 | 32 | 1.8 | 40 |
| H 1001 | 84 | 11.8 | 56 | 5.6 | 42 | 3.4 | 110 | 20.0 | 15 | 42 | 3.4 | 40 |
| H 1501 | 126 | 31.4 | 84 | 14.9 | 63 | 9.1 | 126 | 31.4 | 20 | 63 | 9.1 | 40 |