Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

100% Factory Fire Tested

Efficiency: 84%

Maximum Outlet Temperature: 230°F

Minimum Non-Condensing Inlet Temperature: 105°F

Thermal Shock Proof Heat Exchanger

Footprint: Less Than 5-1/2 ft2

Limited Twenty-Year Thermal Shock Warranty

Limited Ten-Year Heat Exchanger Warranty

Ten-Year Unconditional Burner Head Warranty

Operation Status Center and Full Diagnostic Panel

#### Heat Exchanger

Bronze Headers

ASME Inspected and Stamped
160 PSIG Working Pressure

National Board Approved

Copper-finned Tubes

ASME Steel Tube Retainer

Silicone High Temp O-Rings

60 PSIG ASME Pressure Relief Valve

Temperature and Pressure Gauge,
Shipped Loose

#### Control

120V, 60Hz, Power Supply

120/24V 60Hz Transformer

100% Pilot Shutoff/Lockout

Electronic Intermittent Ignition Pilot (IID)

High Limit Control, Manual Reset

High Limit Control, Auto Reset

On/Off Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Time Delay Pump Off Control

Central Point Wiring Diagnostics Panel

#### Burner

Aerodynamically Stabilized
Non-Clog  Burner

Ultra-Low NOx: Less than 30 PPM

#### Gas Train

Fuel

Natural Gas

Propane (Models 751 & 1001)

Manual Gas Shut-off Valves

Gas Pressure Regulator

Safety Shut-off Valve

Firing Control Valve

Manual Low Gas Pressure Switch

On/Off Firing Mode (H4)

Design Certified ANSI Z21.13/
CSA 4.9

#### Construction

Indoor/Outdoor Construction

Front Controls Enclosed

PolyTuf Powder Coat Finish

Connections (Water, Electrical, Gas)

Rear – Standard

Right Side – Option A-8

#### Venting

Vent Location

Rear – Standard

Right Side – Option Z-2

Vent Termination Cap

Outdoor - Option D-11

Indoor, Horizontal – Option D-15

Indoor, Vertical (by others)

#### Temperature Controls

B-20	Single-Stage Controller, 
100-200°F

B-6	2-Stage Controller, 100-200°F

B-21	4-Stage TempTracker Digital Controller, Loose

B-23	4-Stage TempTracker Digital Controller, Outdoor Reset, Loose

Y-241	Electronic Sequencer, 
1-4 Stages

Y-281	Electronic Sequencer, 
5-8 Stages

#### Additional Safety Controls (Optional)

F-10	Low Water Cut-off, 
Remote Probe

S-2	Manual High Gas Pressure Switch

#### Regulatory Agency Requirements

C-5	Ignition Lockout Module

#### Other Equipment

Condensing Heat Exchanger

Pump

ADB – Type H

Models 751-1501	Model

| Model | MBTUH | B | D | E | F | G | H | K | M | P | Ship Weight | Foot-print | Amps* |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Input | Output | Height |  |  |  | NPT | NPT | Flue ( |  |  | (Lbs.) | (Ft2) |  |
| H 751 | 750 | 630 | 64 | 38 | 44-1/2 | 29-3/4 | 1-1/2 | 2 | 8 | 17-3/4 | 41 | 680 | 5.4 | 8 |
| H 1001 | 999 | 840 | 72 | 46 | 52-1/2 | 37-3/4 | 1-1/2 | 2-1/2 | 10 | 21-1/2 | 49 | 720 | 5.4 | 10 |
| H 1501 | 1499 | 1260 | 82 | 56 | 62-1/2 | 47-3/4 | 1-1/2 | 2-1/2 | 12 | 20-1/4 | 59 | 780 | 5.4 | 12 |
| Dimensions are in inches. Ratings shown are for elevations up to 5,000 feet. For installations at elevations above 5,000 feet, please consult the factory for additional instructions. For direct vent applications, please contact the factory about relocating the pump. | * Current draw does NOT include pump. (Supply breaker must have delayed trip.) |

RATES OF FLOW AND PRESSURE DROPS

|  | 20°F (T | 30°F (T | 40°F (T | Maximum Flow | Minimum Flow |
| --- | --- | --- | --- | --- | --- |
| Model | GPM | (P (ft.) | GPM | (P (ft.) | GPM | (P (ft.) | GPM | (P (ft.) | (T (°F) | GPM | (P (ft.) | (T (°F) |
| H 751 | 63 | 5.8 | 42 | 2.9 | 32 | 1.8 | 110 | 17.0 | 11 | 32 | 1.8 | 40 |
| H 1001 | 84 | 11.8 | 56 | 5.6 | 42 | 3.4 | 110 | 20.0 | 15 | 42 | 3.4 | 40 |
| H 1501 | 126 | 31.4 | 84 | 14.9 | 63 | 9.1 | 126 | 31.4 | 20 | 63 | 9.1 | 40 |

# Text boxes

# ADB™ - Type H

## Hydronic Heating Boilers

Models 751-1501

Certified Clearances

Front	24” (for service)

Rear	12” (water side)

Right	1”

Left	1”

Top	0” (see note 1)

Floor	0” (see note 2)

Vent	1”

Notes:

1.	24” required for service

2.	DO NOT install on carpeting

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com