# XTherm™ - Type WH

## Water Heaters
Models 1005-2005

# XTherm™ - Type WH

## Water Heaters
Models 1005-2005

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 97% Thermal Efficiency at Full Rate; Up to 99% at Part Load

- 100% Factory Fire Tested

- Maximum Outlet Water Temperature: 190°F

- Minimum Acceptable Inlet Water Temperature: 50°F

- Full Safety Diagnostics with History

- Footprint: Less Than 10.8 ft2

- Limited Twenty-Five-Year Thermal Shock Warranty

- Limited Five-Year Copper/Ten-Year Cupro-Nickel Primary Heat Exch. Warranty

- Limited Five-Year Condensing Heat Exchanger Warranty

- Full Electronic Modulation, Constant Ratio 4:1 Turndown

Proudly Made in the USA

Proudly Made in the USA

Modulating Controller with LCD Display

- Status Display Lights

#### Heat Exchanger

Bronze Headers

ASME HLW Stamped; 160 PSIG MAWP

National Board Listed

Fin Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Powder-Coated Tube Sheet

Silicone High Temp O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

150 PSIG – Option A-16

150 PSI Air Vent, Auto

T&P Gauge, Shipped Loose

Stainless Steel Condensing Heat Exchanger

Stainless Steel Evaporator Plate

Boiler Pump: Bronze, 120V, 1, 60Hz
Water Hardness:       GPG

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

Ignition Module

3-Try – Standard

Single-Try – Option C-6

Hot Surface Ignition (HSI)

Remote Flame Sensor

Fixed High Limit, Manual Reset, 200ºF

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Combustion Air Proving Switch

Freeze Protection

Pump Switch

Pump Time Delay

Alarm Dry Contact

- Control (cont.)

Diagnostics Panel with LCD Display,

- 2 lines, 20 characters

Modulating Temperature Control

Water Temperature Sensors (3)

Cold Water Protection

Blocked Condensate Switch

#### Burner

Ultra-Low NOx: Less than 20 PPM

- (Natural Gas Only)

#### Gas Train

- Fuel

- Natural Gas

Propane

- Zero Governor Regulator

- Dual-Seat Combination Valve

- Electronic Modulating Firing Mode (WH7)

#### Construction

- Indoor/Outdoor Construction

- Front Controls Enclosed

- PolyTuf Powder Coat Finish

- Rear Connections (Water, Gas, Vent,

- Electrical, Comb. Air, Cond. Drain)

- Combustion Air Filter

- Design Certified ANSI Z21.10.3/CSA 4.3

- CSA Low Lead Certified ≤ .25 Lead

- Front Connection Low-Voltage Wiring

#### Venting

- Vent Termination, Cat IV

- Outdoor or Indoor, Vertical –

Option D-11 
 Indoor, Horizontal – Option D-15

- Extractor – Optional, Cat II

By others

- Not required

- Multi-Heater Digital Temp Controllers

- B-36	TempTracker Mod+ Hybrid,

- 2-4 Heaters

- B-37	TempTracker Mod+ Hybrid,

5-10 Heaters

B-38 	TempTracker Mod+ Hybrid,
11-16 Heaters

B-45	Multi-Mod Platinum,
2-4 Heaters

B-46	Multi-Mod Platinum EMS,
2-4 Heaters

B-47	Multi-Mod Platinum BACNet,
2-4 Heaters

B-48	Multi-Mod Expansion Module,
1-8 Additional Heaters

#### Options

D-32	PVC Vent Adapter,
Factory-mtd ONLY

- D-33	Polypro Vent Adapter,

Factory-mtd or Field-mtd

I-3	High Limit, Auto Reset,

Adj., 40-180F

I-5	High Limit, Manual Reset, Adj.,

100-200F

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch,

Manual Reset

Z-12	Condensate Neutralizer Kit

#### Regulatory Agency Requirements

XTherm – Type WH

Models 1005-2005	Model

NOTE:  Primary/Secondary plumbing is mandatory for proper operation.

NOTE:  Primary/Secondary plumbing is mandatory for proper operation.

CLEARANCES (in.)

|  | Front | Rear | Right | Left | Top | Floor | Vent |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Certified Minimum | 24 | 12 | 1 | 1 | 0 | 0 | 1 |
| Minimum Service | 24 | 36 | 24 | 1 | 10 | N/A | N/A |

POWER REQUIREMENTS – AMPS†

| Model (WH7-) | Heater Amp Draw † | Pump Amp Draw † |  |  |
| --- | --- | --- | --- | --- |
|  |  | Soft | Medium | Hard |
| 1005 | 12** | 10 | 10 | 14 |
| 1505 | 12** | 10 | 14 | 17 |
| 2005 | 18** | 17 | 17 | N/A |

† Separate power connections are factory supplied and separate supply breakers must be field supplied.

** Current draw is for heater only (Supply breaker must have delayed trip).

| Model (WH7-) | MBTUH |  | Dimensions (in) |  |  |  |  |  |  |  |  |  |  |  | Ship Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B Height | D | E | F | G* NPT | K Flue Ø | L | M | N C/A Ø | P | R | Y |  |
|  | Input | Output |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1005 | 999 | 969 | 55-1/8 | 45 | 47-1/8 | 36-1/2 | 1-1/4 | 6 | 40-1/16 | 11-1/2 | 6 | 47-1/8 | 8-1/16 | 6-1/16 | 1065 |
| 1505 | 1500 | 1455 | 67-1/8 | 57 | 59-1/16 | 38-1/2 | 1-1/4 | 8 | 52-1/16 | 12-5/8 | 8 | 59-1/8 | 8-3/16 | 6-1/16 | 1234 |
| 2005 | 1999 | 1939 | 81-1/8 | 71 | 71-3/16 | 38-1/2 | 2 | 8 | 64-1/16 | 12-5/8 | 8 | 73-1/8 | 8-3/16 | 6-1/4 | 1461 |

| Note: Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions. | * For Propane Gas, all models are 1” NPT |
| --- | --- |

| Model (WH7-) | RECOVERY RATES |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |
|  | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |
| 1005 | 5817 | 3878 | 2908 | 2327 | 1939 | 1662 | 1454 | 1293 | 1163 |
| 1505 | 8733 | 5822 | 4367 | 3493 | 2911 | 2495 | 2183 | 1941 | 1747 |
| 2005 | 11639 | 7759 | 5813 | 4656 | 3880 | 3325 | 2910 | 2586 | 2328 |