Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     	 Indoor

LOW NOx

- Less than 40 nanograms per joule

EFFICIENT

- 82% efficiency – highest of any atmospheric boiler
available today

THERMAL SHOCK PROOF

- Twenty-year warranty against thermal shock damage
up to 150°F differential

- Maximum operating temperature: 230°F

LIGHTWEIGHT

- A floor load of 70 lbs./sq. ft. or less

HIGH RECOVERY

- Cuts fuel costs substantially because the standby and
radiation losses normal to other boilers and
tank-type water heaters are eliminated

LOW WATER OPERATING TEMPERATURE

- Operates with water temperature as low as
105°F without condensing

#### Heat Exchanger

ASME Inspected and Stamped
160 PSIG

National Board Approved

Headers

Cast Iron Glass-lined – Standard

Bronze – Option A-1

Finned Tubing

Copper – Standard

Cupro Nickel – Option A-3

ASME Steel Tube Sheet

Silicone O-Rings

ASME Pressure Relief Valve

45 PSIG – Standard

PSIG ASME – Optional

Temperature and Pressure Gauge, Shipped Loose

Water Connections

Left Hand – Standard

Right Hand – Option A-6

Flow Configuration – Two-pass

Pump – Optional

Mounted, 1/8 HP, 120 V, 1(( 60 Hz

#### Controls

120V, 60Hz, 1 Ph Power Supply

120/24V Transformer

100% Pilot Shut-off/Lockout

Electronic, Intermittent Ignition (IID) Pilot

#### Controls (cont'd)

High Limit Control, Manual Reset

On/Off Switch

Flow Switch

Economaster II Pump Time Delay

Electronic Outdoor Reset Control

( Models 181 & 261)

#### Gas Train

Natural Gas

Manual Main Gas Shut-off Cock

Main Gas Pressure Regulator

Redundant Safety Shut-off Valve

Control Valve

Firing Mode

On/off (H4)

Two-stage firing (H3)

Design Certified

ANSI Z21.13 /CSA 4.9

#### Construction

Front Controls

Stainless Steel, Fan-Assisted Burners

Polytuf Powder Coat Finish

Draft Diverter

Base – Optional

Combustible Floor Shield – 
Option J-1

#### Temperature Controls

B-6	2-stage Aquastat – 
100-200ºF

B-26	2-stage Digital Controller

B-27	2-stage Digital Controller, Outdoor Reset

B-___	Temp Tracker Digital Controller, 2 Stage

B-___Temp Tracker Digital 
Controller, 4 Stage

B-42   Electronic Outdoor Reset

Controller (Std. on Models 181&261)

#### Additional Safety Controls

F-10	Low Water Cut-off Probe

I-1	High Limit Control, Auto Reset

S-1	Low Gas Pressure Switch

S-2	High Gas Pressure Switch

#### Regulatory Agency Requirements

Raytherm - Type H

Hydronic Heating Boilers - Indoor	Model

|  |  |  |  | Dimensions (Inches) | Shipping Weight (Lbs.) – Approx. |
| --- | --- | --- | --- | --- | --- |
| Model No. | MBTU Input | MBTU Output | AFUE (%) | Width A | Height C | J | Flue Dia. K |  |
|  |  |  |  |  |  |  |  | No Pump | w/ Pump |
| H-181* | 181 | 148 | 82.6 | 18-1/4 | 62-5/8 | 12-1/16 | 6 | 191 | 221 |
| H-261 | 264 | 216 | 82.7 | 22-3/8 | 62-7/8 | 11-1/8 | 7 | 214 | 244 |
| H-331 | 334 | 274 | N/A | 25-3/4 | 63-3/4 | 10-3/4 | 8 | 234 | 264 |
| H-401* | 399 | 327 | N/A | 29-1/4 | 65-3/8 | 12-1/2 | 9 | 253 | 283 |

*	 Exceptions on H3 (two-stage-fired) models:

- Model H3-181 has an 18-1/4” gas connection

- Model H3-401 has 375 MBTU Input and 308 MBTU Output

NOTE:	Ratings shown are for elevations up to 2,000 feet. For elevations over 2,000, reduce ratings at the rate of 4% for each 
1,000 feet above sea level.

BOILER RATE OF FLOW AND PRESSURE DROP

| Model No. | 10° (T | 20° (T | 30° (T |
| --- | --- | --- | --- |
|  | GPM | (P FT | GPM | (P FT | GPM | (P FT |
| H-181 | 30 | 4.2 | N/A | N/A | N/A | N/A |
| H-261 | 43 | 8.5 | 22 | 2.2 | N/A | N/A |
| H-331 | N/A | N/A | 27 | 3.4 | N/A | N/A |
| H-401 | N/A | N/A | 33 | 5.2 | 22 | 2.3 |

N/A – Not Applicable

# Text boxes

# Raytherm® - Type H

# Hydronic Heating Boilers

# Models 181-401 - Indoor

Low NOx

Low NOx

*

Raypak, Inc.  (  2151 Eastman Avenue, Oxnard, CA  93030  (  (805) 278-5300  (  Fax (800) 872-9725  (  www.raypak.com