# XTherm® - Type WH

## Water Heaters
Models 1005A-2005A

Job:

Engineer:

Contractor:

Prepared By: 	     		Date:

Model: 	     		Indoor/Outdoor:

- 97% Thermal Efficiency at Full Rate

- 100% Factory Fire Tested

- VERSA IC® Modulating Controller with 7” color touchscreen display

- Raymote™ remote connectivity provided standard

- Soft-Start Ignition; 60% Min Fire

- Full Safety Diagnostics with History

- Status Display Lights

- Cascade up to 4 Heaters – No External Sequencer Required

- Modbus RTU BMS Port

- Maximum Outlet Water Temperature: 180°F

- Maximum Tank Setpoint: 150°F

Limited Twenty-Five-Year Thermal Shock Warranty

Proudly Assembled in the USA

Limited Five-Year Copper/Ten-Year Cupro-Nickel Primary Heat Exch. Warranty

- Limited Ten-Year Secondary Heat Exchanger Warranty

#### Heat Exchanger

Bronze Headers

ASME HLW Stamped; 160 PSIG MAWP

National Board Listed

Fin Tubing

Copper – Standard

A-3 Cupro-Nickel

ASME Powder-Coated Tube Sheet

Silicone High-Temp O-Rings

ASME Pressure Relief Valve

125 PSIG – Standard

PSIG – Optional

Manual Air Bleed Valve

T&P Gauge

Stainless Steel Condensing Heat Exchanger – U stamped

Stainless Steel Evaporator Plate

Boiler Pump: Bronze, 120V, 1, 60Hz
Water Hardness:       GPG

#### Control

120V, 60Hz, 1Ø, Power Supply

120/24V 60Hz Transformer

VERSA IC®

7” color HD touchscreen display

Raymote™ Wi-Fi remote connectivity

Ignition Module

3-Try – Standard

C-6 Single-Try

Remote Flame Sensor

Fixed High Limit, Manual Reset, 200ºF

On/Off Power Switch

Flow Switch

Blocked Vent Pressure Switch

Freeze Protection

Alarm Dry Contact

Pump Outputs – Pilot Duty

System

Programmable Pump Time Delays

Water Temperature Sensors (3)

Cold Water Protection

Blocked Condensate Switch

Modbus RTU BMS Port (Up to 115K Baud Rate, See Cat. 5000.73)

B-85      BMS Gateway, Modbus RTU to     Modbus TCP, N2 Metasys, BACnet IP, or BACnet MS/TP.

B-86      BMS Gateway, Modbus RTU to LonWorks.

#### Burner

Hot Surface Ignition (HSI)

Radially-Fired Knitted Burner

#### Gas Train

Fuel

Natural Gas

Propane (Grade HD-5)

Dual-Seat Combination Valve

Electronic Modulating Firing Mode (WH7)

#### Construction

Indoor/Outdoor Construction

Enclosed Front Controls

PolyTuf Powder Coat Finish

Rear Connections (Water, Gas, Vent, Electrical, Comb. Air, Cond. Drain)

Combustion Air Filter

Design Certified ANSI Z21.10.3/CSA 4.3

CSA Low Lead Certified ≤ .25% Lead

Front Connection Low Voltage Wiring

#### Venting

Vent Termination, Cat IV

D-11 Outdoor or Indoor, Vertical

D-15 Indoor, Horizontal

Extractor – Optional, Cat II

By others

Not required

#### Options

D-32	PVC Vent Adapter, maximum return water temperature allowed 170ºF (Factory Mounted Only)

D-33	Centrotherm® Polypropylene Vent Adapter, maximum return water temperature allowed 190ºF (Includes Manual Vent Limit, Shipped Loose)

F-10	Low Water Cut-Off, Remote Probe

I-6	High Limit, Manual Reset, Adj., 100-200F

I-14	High Limit, Auto Reset, Adj., 40-180°F

S-1	Low Gas Pressure Switch, 
Manual Reset

S-2	High Gas Pressure Switch, Manual Reset

Z-12	Condensate Treatment Kit

#### Additional Options or Accessories

- XTherm – Type WH

Models 1005A-2005A	Model

NOTE:  Use in conjunction with storage tank for proper operation.

CLEARANCES (in.)

|  | Front | Rear | Right | Left | Top | Floor | Vent |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Certified Minimum | 24 | 12 | 1 | 1 | 0 | 0 | 1 |
| Minimum Service | 24 | 36 | 24 | 1 | 10 | N/A | N/A |

POWER REQUIREMENTS – AMPS†

| Model (WH7-) | Heater Amp Draw † | Pump Amp Draw † |  |  |
| --- | --- | --- | --- | --- |
|  |  | Soft 1-4 Gr. | Medium 5-15 Gr. | Hard 16-25 Gr. |
| 1005A | 12 ** | 10 | 10 | 14 |
| 1505A | 12 ** | 10 | 14 | 17 |
| 2005A | 18 ** | 17 | 17 | N/A |

† Separate power connections are factory supplied and separate supply breakers must be field supplied.

** Current draw is for heater only (Supply breaker must have delayed trip).

| Model (WH7-) | MBTUH |  | Dimensions (in) |  |  |  |  |  |  |  |  |  |  |  |  | Ship Weight (Lbs.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | B Height | D | E | F | G* NPT | K Flue Ø | L | M | N C/A Ø | P | R | V | Y |  |
|  | In | Out |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1005A | 999 | 969 | 55-1/4 | 45 | 47 | 37 | 1-1/4 | 6 | 41 | 11-1/2 | 6 | 47-1/8 | 8-5/16 | 13 | 6-1/4 | 1065 |
| 1505A | 1500 | 1455 | 67-1/8 | 57 | 59 | 38-5/8 | 1-1/4 | 8 | 53 | 12-5/8 | 8 | 59-1/8 | 8-3/16 | 13 | 6-1/4 | 1234 |
| 2005A | 1999 | 1939 | 81-1/8 | 71 | 72 | 39-5/8 | 2 | 8 | 65-1/2 | 12-5/8 | 8 | 73-1/8 | 8-3/16 | 10 | 6-1/2 | 1461 |

| Note: Ratings shown are for elevations up to 4,500 feet. For installations at elevations above 4,500 feet, please consult the factory for additional instructions. | * For Propane Gas, all models are 1” NPT |
| --- | --- |

| Model (WH7-) | RECOVERY RATES |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Temperature Rise (°F) |  |  |  |  |  |  |  |  |  |
|  | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 |
| 1005A | 5873 | 3915 | 2936 | 2349 | 1958 | 1678 | 1468 | 1305 | 1175 | 1068 |
| 1505A | 8818 | 5879 | 4409 | 3527 | 2939 | 2519 | 2205 | 1960 | 1764 | 1603 |
| 2005A | 11752 | 7834 | 5876 | 4701 | 3917 | 3358 | 2938 | 2611 | 2350 | 2137 |